## How this works
How this works: |  | The information is organized in tabs.
This is a spread sheet is a synopsis and does not include the complete code language or requirements.
For the text on Fire Flow see the Fire flow information
For the calculations for Fire Flow see the Fire flow worksheet
The chapter 9 tab lists other reasons for sprinkler system that are required by the International Building Code
See the Fire Alarm Worksheet for information on when fire alarm are required by the International Building Code
The special occupancy tab for fire alarm is not complete at this time if you have a unique occupancy or portion of an occupancy. Verify in the code that there are no other fire alarm requirements

## Fireflow worksheet
Fill in the blue-green boxes |  |  | Sprinkler systems are required in all structures over 12000 square feet (this area may be increased as specified in 506) and over 7500 square feet in the UGA |  |  | version 10/22/13
Enter the building size | Most Stringent Occupancy | Jurisdiction | Is a fire sprinkler system required by chapter 9? Answer questions in Chapter 9 tab
357212 | S1 | County | Yes
Read the yellow areas for fire flow information
|  | Construction Type | [9 empty] | GPM
| I or II-FR | IIA or IIIA | IV HT or VA | IIB or IIIB | VB |  |  |  |  | I or II-FR | IIA or VA | IV HT or VA | IIB or IIIB | VB
Fire flow based square footage and building type | 6000 | 6000 | 8000 | 8000 | 8000 |  | added interpolation section 11/30/10 |  |  | 0 | 0 | 0 | 0 | 0
Surcharge or credit based on occupancy | 600 | 600 | 800 | 800 | 800 |  | corrected minutes for flow over 2000 gpm |  |  | 0 | 0 | 0 | 0 | 0
Unmitigated Fire Flow | 6600 | 6600 | 8800 | 8800 | 8800 | 2011-04-01 | corrected minutes for tank size if oover 3000 gpm |  |  | 0 | 0 | 0 | 0 | 0
Only tank used to mitigate fire flow of 2000 or less gallons | 0 | 0 | 0 | 0 | 0 | 2013-06-18 | corrected cell line 18 formula |  |  | 0 | 0 | 0 | 0 | 0
Only tank used to mitigate fire flow of more than 2000 gallons | 792000 | 792000 | 1056000 | 1056000 | 1056000 | 2013-10-22 | revised for new 2012 code |  |  |  |  | 0 | 0 | 0
Test occupancy for H | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 6000 | 6000 | 8000 | 8000 | 8000
Test occupancy for I | 1 | 1 | 1 | 1 | 1 | 2022-02-01 | added lines to enter water available on site
Test Limited systems (4 head design ) may be used when GPM is less than 1500 | No | No | No | No | No
Sprinkler reduction 50% | 3300 | 3300 | 4400 | 4400 | 4400
test for under 500 gallons
Fire Alarm reduction -250= GPM Hydrant or Tank | -250 | -250 | -250 | -250 | -250 |  |  |  |  | No Fire Flow Required
Mitigated fire flow -additional gpm required if more than 500 | 3050 | 3050 | 4150 | 4150 | 4150
enter gallons available at water system hydrants using a minus sign for the number | -2000 | -2000 | -2000 | -2000 | -2000
Remaining gallons via a tank | 1050 | 1050 | 2150 | 2150 | 2150
Is a fire alarm required? | yes | yes | yes | yes | yes
Chapter 9 sprinklers required? | 1 | 1 | 1 | 1 | 1
UGA or County | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 6000 | 6000 | 8000 | 8000 | 8000
UGA requires sprinklers @7500 square feet. Zero = no, One = yes | 1 | 1 | 1 | 1 | 1
County requires sprinklers @ 12,000 square feet Zero = no, One = yes | 1 | 1 | 1 | 1 | 1
Additional Water required on site to mitigate fire flow due for UGA/ County Limits or to meet the requirements in Chapter 9. | yes | yes | yes | yes | yes
Tank size if less than 2000 GPM | 63000 | 63000 | 0 | 0 | 0
Tank size if more than 2000 GPM | 0 | 0 | 258000 | 258000 | 258000
Tank size if more than 3000 GPM | 0 | 0 | 387000 | 387000 | 387000
NA=not applicable
[6 empty] | 366000 | 498000 | 498000 | 498000
[6 empty] | 183000 | 249000 | 249000 | 249000
Yes
No
Surcharge test
0
0
0
0
| 0.1 |  |  | GFM | I or II-FR | IIA or VA | IV HT or VA | IIB or IIIB | VB
| 0 |  |  | 500 | 5500 | 3700 | 2600 | 2100 | 1600
| 0 |  |  | 750 | 7800 | 5000 | 3500 | 2700 | 2000
| 0 |  |  | 1000 | 11100 | 6800 | 4700 | 3500 | 2400
|  |  |  | 1250 | 15900 | 9300 | 6200 | 4500 | 2900
|  |  |  | 1500 | 22750 | 12700 | 8200 | 5900 | 3600
|  |  |  | 1750 | 30200 | 17000 | 10900 | 7900 | 4800
|  |  |  | 2000 | 38700 | 21800 | 12900 | 9800 | 6200
| 0.1 |  |  | 2250 | 48300 | 24200 | 17400 | 12600 | 7700
|  |  |  | 2500 | 59000 | 33200 | 21300 | 15400 | 9400
|  |  |  | 2750 | 70900 | 39700 | 25500 | 18400 | 11300
|  |  |  | 3000 | 83700 | 47100 | 31100 | 21800 | 13400
|  |  |  | 3250 | 97700 | 54900 | 35200 | 25900 | 15600
|  |  |  | 3500 | 112700 | 63400 | 40600 | 29300 | 18000
|  |  |  | 3750 | 128700 | 72400 | 46400 | 33500 | 20600
|  | Occupancy Types |  | 4000 | 145900 | 82100 | 52500 | 37900 | 23300
|  | A1 |  | 4250 | 164200 | 92400 | 59100 | 42700 | 26300
|  | A2 |  | 4500 | 183400 | 103100 | 66000 | 47700 | 29300
|  | A3 |  | 4700 | 203700 | 114600 | 73300 | 53000 | 32600
|  | A4 |  | 5000 | 225200 | 126700 | 81100 | 58600 | 36000
|  | A5 |  | 5250 | 247700 | 139400 | 89200 | 65400 | 39600
|  | B |  | 5500 | 271200 | 152600 | 97700 | 70600 | 43400
|  | E |  | 5750 | 295900 | 166500 | 106500 | 77000 | 47400
|  | F1 |  | 6000 | u | u | 115800 | 83700 | 51500
|  | F2 |  | 6200 | u | u | 125500 | 90600 | 55700
|  | H1 |  | 6500 | u | u | 135500 | 97900 | 60200
|  | H2 |  | 6750 | u | u | 145800 | 106800 | 64800
|  | H3 |  | 7000 | u | u | 156700 | 113200 | 69600
|  | H4 |  | 7250 | u | u | 167900 | 121300 | 74600
|  | H5 |  | 7500 | u | u | 179400 | 129600 | 79800
|  | I1 |  | 7750 | u | u | 191400 | 138300 | 85100
|  | I2 |  | 8000 | u | u | u | u | u
I3
I4
M
R1
R2
R3
S1
S2
U
Occupancy Types
| A1 |  |  |  | UGA
| A2 |  |  |  | County
A3
A4
A5
B
E
F1
F2
H1
H2
H3
H4
H5
I1
I2
I3
I4
M
R1
R2
R3
S1
S2
U

## Chapter 9 sprinkler check
Test for Chapter 9 fire area sprinkler system
Pick yes or no
Is the A1,A2, A3 or A4 occupant load greater than 300 or is it on a floor other than the exit discharge? | yes | yes, supression system required | 1
Does the A1 fire area contain a multi-theatre complex? | no | no fire area sprinklers required | 0
Does the A2 fire area exceed 5000 square feet? | no | no fire area sprinklers required | 0
Does any fire area meet the definition of a night club? | no | no fire area sprinklers required | 0 | [10 empty] | 0
Does the A2 fire area have an occupant load of 100 or more. | no | no fire area sprinklers required | 0 | [10 empty] | 0
Does the A5 fire area contain concession stands, retail areas, press boxes, and accessory areas greater than 1000 square feet? | no | no fire area sprinklers required | 0 | [10 empty] | 0
Is this an E occupancy with any classroom having an occupant load greater than 50, are separated portable classrooms in a cluster greater than 5000 square feet? | no | no fire area sprinklers required | 0 | [10 empty] | 0
Is this an S1, M, or F1 fire area that is three or more stories above grade? | no | no fire area sprinklers required | 0 | [10 empty] | 0
Does the F1 woodworking in an area greater than 2500 square feet create fine dust? | no | no fire area sprinklers required | 0 | [10 empty] | 0
Is the M occupancy located more than three stories above grade plane? | no | no fire area sprinklers required | 0 | [10 empty] | 0
Does the M occupancy contain high piled combustible storage? | no | no fire area sprinklers required | 0 | [10 empty] | 0
Is the repair garage located in a basement? | no | no fire area sprinklers required | 0
Are there windowless stories? | no | no fire area sprinklers required | 0
Is there any bulk storage of tires? | no | no fire area sprinklers required | 0
Is the S-2 a commercial truck or bus garage exceeding 5000 square feet? | no | no fire area sprinklers required | 0
Is this an R or H occupancy? | no | no fire area sprinklers required | 0
[9 empty] | 0 | 0 | 0 | 0 | 0
Is this ambulatory care? | no | no fire area sprinklers required | 0
Is there wood working over 2500 square feet? | no | no fire area sprinklers required | 0
1
Surcharge test
#REF!
#REF!
#REF!
#REF!
| #REF! |  | GFM | I or II-FR | IIA or VA | IV HT or VA | IIB or IIIB | VB
| #REF! |  | 500 | 5500 | 3700 | 2600 | 2100 | 1600
| #REF! |  | 750 | 7800 | 5000 | 3500 | 2700 | 2000
| #REF! |  | 1000 | 11100 | 6800 | 4700 | 3500 | 2400
|  |  | 1250 | 15900 | 9300 | 6200 | 4500 | 2900
|  |  | 1500 | 22750 | 12700 | 8200 | 5900 | 3600
|  |  | 1750 | 30200 | 17000 | 10900 | 7900 | 4800
|  |  | 2000 | 38700 | 21800 | 12900 | 9800 | 6200
| #REF! |  | 2250 | 48300 | 24200 | 17400 | 12600 | 7700
|  |  | 2500 | 59000 | 33200 | 21300 | 15400 | 9400
|  |  | 2750 | 70900 | 39700 | 25500 | 18400 | 11300
|  |  | 3000 | 83700 | 47100 | 31100 | 21800 | 13400
|  |  | 3250 | 97700 | 54900 | 35200 | 25900 | 15600
|  |  | 3500 | 112700 | 63400 | 40600 | 29300 | 18000
|  |  | 3750 | 128700 | 72400 | 46400 | 33500 | 20600
|  |  | 4000 | 145900 | 82100 | 52500 | 37900 | 26300
|  |  | 4250 | 164200 | 92400 | 59100 | 42700 | 29300
|  |  | 4500 | 183400 | 103100 | 66000 | 47700 | 32600
|  |  | 4700 | 203700 | 114600 | 73300 | 53000
|  |  | 5000 | 225200 | 126700 | 81100 | 58600
|  |  | 5250 | 247700 | 139400 | 89200 | 65400
|  |  | 5500 | 271200 | 152600 | 97700 | 70600
|  |  | 5750 | 295900 | 166500 | 106500 | 77000
|  |  | 6000 | u | u | 115800 | 89700
|  |  | 6200 | u | u | 125500 | 90600
|  |  | 6500 | u | u | 135500 | 97900
|  |  | 6750 | u | u | 145800 | 106800
|  |  | 7000 | u | u | 156700 | 113200
|  |  | 7250 | u | u | 167900 | 121300
|  |  | 7500 | u | u | 179400 | 129600
|  |  | 7750 | u | u | 191400 | 138300
|  |  | 8000 | u | u | u | u | u
#REF!
no
yes
Occupancy Types
| A1 |  |  | UGA
| A2 |  |  | County
A3
A4
A5
B
E
F1
F2
H1
H2
H3
H4
H5
I1
I2
I3
I4
M
R1
R2
R3
S1
S2
U

## fire alarm worksheet
Fire Alarm and Detection |  |  | Red is automatic | Blue is manual only
Credit for fire flow requires an Automatic Fire Alarm system with full coverage and central station monitoring
No autodetection devices and annunication devices are required. |  |  |  | See section 907.9.1 and 907.9.2 for location and type of devices required.
Auto Heat detection not required where the sprinklers are connected to the FA panel.
Automatic fire detectors shall be smoke detectors unless ambient conditions prohibit the installation
Group A | MANUAL Alarms - A single pull station may be used where sprinklers are installed throughout the building and the sprinkler system is connect to an FA panel
Occupant load of 300 or more. This is an aggregate load unless fire barriers separate the assembly areas. If used for group E, a group E - FA system is required.
Voice communication required when the occupant load is 1000 or more.
Live voice not to exceed three minutes may over ride
Emergency power is required.
Group B | MANUAL Alarms - A single pull station may be used where sprinklers are installed throughout the building and the sprinkler system is connect to an FA panel
Occupant load over 500 or more
Occupant load over 100 above or below the exit discharge
See the code for ambulatory health care facilities.
Group E | MANUAL Alarms - A single pull station may be used where sprinklers are installed throughout the building and the sprinkler system is connect to an FA panel
Except occupant loads 30 or less
Exception- pull stations are not required when:
interior corridors have smoke detectors with alarm verification
Assembly spaces are protected with detection devices
Spaces with dust and vapors have detectors
central evacuation signal is provided
central station monitoring is provided
two way communication is provided
Group F | MANUAL Alarms - A single pull station may be used where sprinklers are installed throughout the building and the sprinkler system is connect to an FA panel
Two or more stories or when an occupant load over 500 or more above or below the exit discharge
Group H | Manual fire alarm systems in H5 Occupancies and manufacturing
Automatic detection where covered under IFC chapter 37, 39, or 40.
Group I | Manual - see 907.2.6
Group I-1 | Automatic | not required for exterior balconies
MANUAL Alarms - A single pull station may be used where sprinklers are installed throughout the building and the sprinkler system is connect to an FA panel
Refer to 907.2.10.1.3 for Fire Alarm requirements
Group I-2 | Automatic | see exceptions 907.2.6.2
Group I-3 | Automatic and Manual |  | see section 907.2.6
Presignal systems shall not be used.
Group M | MANUAL Alarms - A single pull station may be used where sprinklers are installed throughout the building and the sprinkler system is connect to an FA panel
Occupant load over 500 or more
Occupant load over 100 above or below the exit discharge
Covered Mall Buildings
Occupant notification can be at a monitored station with voice communication
Group R-1 | MANUAL Alarms - A single pull station may be used where sprinklers are installed throughout the building and the sprinkler system is connect to an FA panel
Manual systems may be omitted if not more than two stories with noncontiguous spaces and one hour separation of units with direct exit to the exterior and separated from public areas
Automatic fire systems are required in interior corridors unless each unit has a direct exit.
Group R-2 | MANUAL Alarms - A single pull station may be used where sprinklers are installed throughout the building and the sprinkler system is connect to an FA panel
Manual systems may be omitted if not more than two stories with noncontiguous spaces and one hour separation of units with direct exit to the exterior and separated from public areas
manual fire systems are required in interior corridors unless each unit has a direct exit.
Refer to 907.2.9 for Fire Alarm requirements
Group R-3 | Refer to 907.2. 10 for Fire Alarm requirements
Group R-4 | Refer to 907.2.9 for Fire Alarm requirements
Refer to the code for special occupancies - Amusement Highrise, Atruims, High piled combustible Areosal storage Lumber Underground Residential aircraft hangers Battery rooms Control towers Duct detectors
Review the code requirements for CO2 devices in residential occupancies

## interplation (hidden)
interpolation worksheet |  | For square footage between the gpm, interpolation is allowed when using a credit to gain square footage or if the gpm is limited. | Fill in the yellow boxes from the information on the chart in tab 1
| gallons per minute 2 | 2000 | GPM 2 | 6200
| gallons per minute 1 | 1750 | GPM 1 | 4800
Interpolation applies where no credit is available
|  | desired square footge | 5600 |  |  |  | increase in using the percent
|  | 2000 | 6200
|  | 1750 | 4800
|  | gallons | square feet |  | gallon per square foot
|  | 250 | 1400 |  | 0.17857 |  | 5600
|  | percentage increase in decimal |  |  |  |  | -4800
|  | 0.2 |  |  |  |  | 800
|  | gallons with increase | times square feet per gallon |  | allow square footage |  | 142.8571
1892.8571
|  | minimum gpm * increase percentage | feet *increase+feet
|  | 1750 | 312.5 |  | 2062.5 | 1031.25
-378.5714
[5 empty] | 800 |  | 1514.2857

## reverse eng (hidden)
Do not use not complete
Take maximum gpm x surcharge to determine the added gpm
take the max square footage
1750 | 150 | 1600 | 12640000 | 7222.8571
7900
1500/5900=1350*x
1500x=1350*5900
7965000
5310

## for later (hidden)
|  |  | gpm available |  |  | max square footage |  | Type II construction |  | occu | surcharge %
| Logic | if only | 1500 | gpm is available for |  | 5900 | for | II | based on an | S1 | 0.1
| deduct the square footage for the surcharge = |  |  |  | 150 | x | 0.17857 | = | 26.7857
| The difference between the lower and upper gpm is |  |  |  |  | 1250 | 250
1500
| the difference between the lower and upper square footage is |  |  |  |  | 4500 | 1400
5900
| square footage / gpm | [5 empty] | 5.6 | 1400 | 140 | 5760
250 | gpm/ square footage | [5 empty] | 0.17857 | 250 | 25 | 1475 | 263.3929
| max square footage less deduction for the surcharge = |  |  |  |  | 5873.2143